Levtron Instruments Pvt Ltd

Office No 02, 1” Floor, Plot No 6,

Sr. No. 78/1, Pandhari Industrial Estate, Shivane, Pune-411023

9730042725 /9579430012

Sales@levtron.in

1.www.levtron.in

2.www.levtonintruments.com

LULT-2300L- 5M  D  4  N   NE  NC

Example LULT-2300L-5-D-4-N-NE-NC

Measuring range: 0-5m, power supply 24VDC， Output :4- 20MA ，display No display with No Explosion-proof and No Corrosion-proof

NC：No Corrosion-proof C：Corrosion-proof

Corrosion-proof class

NE：No Explosion-proof EX：Explosion-proof

Explosion-proof class

N：No display E：LED D： LCD

Display

4：4~20MA	H：Hart

RS：RS485	AV0:0-5VDC AV2：0-10VDC	 AV3:1-10VDC

Output signal

A:220V，D:24VDC，D1:12VDC

Supply voltage

1,2,3	10,15,20,30,40(MAX)

Range pressure

LULT-2300L

Product category

Selection table

Ultrasonic level measuring instrument, taking the advantages of various many level measuring instruments, is a universal one characterized by total digitalized and humanized design. It has perfect level monitoring, data transmission and man-machine communication. It is featured by strong anti- interference performance; free setting of upper and lower limits and online output regulation, on-site indication, optional analog, switching value, and RS485 output and easy connection with main unit. The cover, made of waterproof engineering plastics, is small and firm with ABS probe. Therefore, it is applicable for various fields concerning level measuring and monitoring. According to the practical situation, it also can add other modules, such as RS 485, current output; it can be match with PLC better.

| Technical Parameters |  |
| --- | --- |
| Comprehensive accuracy | 0.3%F.S |
| Blind spot | ＜0.4-1.8m（different for range） |
| Medium | Well water, fire water tank, river water, tap water, etc. |
| Working temperature | normal temperature, normal pressure |
| Warranty period | 12 months |
| Frequency | 20～350KHz |
| Power supply | 12-24VDC |
| Output signal | 4～20mA RL>600Ω（standard）,1～5V\1～10V,RS485 2 NPN,2 relays (AC: 5A 250V DC: 10A 24V) |
| Housing material | ABS |
| Power consumption | <1.5W |
| Dimension | Φ92mm×198mm×M60/79mm×300mm×DN80 |
| Sealing class | IP65(others optional) |

LULT-2300L-B1               LULT-2300L-C1	       LULT-2300L-D1

Wiring Diagram

Definition of lead

pin／color

applied

Supply -

⑥DC12~24V-

Yes／□No

Supply +	⑤DC12~24V+	Yes／□No

Voltage output

□Yes／□No

Current output	⑨4~20mA	Yes／□No

Serial output	③RS485(A)	□Yes／□No

Output controlⅠ

①J1_COM

②J1_NO

□Yes／□No

④RS485(B)

Wiring diagram of current (voltage) output connecting with secondary instrument

serial output connecting with PC

NPN output wiring diagram

Relay output setting：

This instrument has 2 relays or 3 NPN output. When uses relay control, it must be set control point: D and H. D for relay start point, H for

relay end point. X for display value. It works as follows:

| X﹤D close | D | D<X<H retain | H | X﹥H Disconnect |
| --- | --- | --- | --- | --- |

| X﹥D close | D | D>X>H retain | H | X﹤H Disconnect |
| --- | --- | --- | --- | --- |

When D﹤H when D﹥H